November 19, 2004

Comments on

“Draft Work Plan; Landfill Gas System Expansion; Operable Unit 2 Landfills; Former Fort Ord, California”

Prepared by Dr. Peter L. deFur

Environmental Stewardship Concepts

1108 Westbriar Dr., Suite F

Richmond VA 23238

Comments prepared for the Fort Ord Administrative record

These comments were prepared at the request of the Fort Ord Environmental Justice Network (FOEJN) to provide technical comment to the Army and summarize the report on landfill gas expansion for the community. FOEJN represents the affected community in the greater Fort Ord area in the clean up of contamination and ordnance related waste.

Mention of any trade name or commercial product or company does not constitute endorsement by any individual or party that prepared or sponsored this report.

This Draft Work Plan explains that the Army will install additional gas vents and pumps to extract and destroy the gases that are produced by the Landfill in area F.  Area F is the section that was created when the Army moved the landfill from across Imjin Highway.  This section of the landfill now produces methane and a number of volatile organic compounds that are poison gases.

The Army has decided that the landfill gases coming out of and underneath Area F at the Operating Unit 2 Landfill need to be collected and treated more than the present system collects and treats.  This new system will add 23 new gas wells that extract the gases from the landfill.  Eighteen (18) of these wells will be placed along the perimeter of the area. Especially along the north, south and western borders of the landfill. Five (5) wells will be placed in the interior of the landfill area.

None of the new wells will be placed around the remainder of the landfill areas, the older areas, labeled areas B, C, D and E.

The gases will no longer be treated by a filter system, which does not treat methane well.  Instead, the gases will be burned off using a gas burner that destroys the organic compounds and the methane.

This step is a positive one for the Army to take and should result in a great reduction in the amount is gas that is released from the landfill. In addition, the use of the burner is intended to destroy the gases once collected, rather than release methane (which causes global warming).

The Work Plan notes that the present system does not operate all the time, but only 100 hours every two weeks.  It is not clear why the present system is not operating all the time, but that is another matter.  The new system should be operated as much as possible, with time for maintenance.  During maintenance, the system should have a backup system, one that will also provide emergency treatment in case the primary system fails or needs more than a short shutdown for maintanence.

The report refers to vinyl chloride gas.  This gas is highly toxic and a serious problem for human health.  Page 2-3,section 2.2.1, item #1 refers to vinyl chloride possibly appearing in groundwater in the future.  The report needs to offer more explanation of why vinyl chloride may be appearing in groundwater in the future.

Page 3-2, section 3.2.2 refers to a risk assessment that was conducted fort he gas burner. The Army needs to make this risk assessment available to the public to review and comment, as it is an important part of the documentation for this work.

Page 6-3, section 6.2 states that the gas pumps will operate round the clock for a week to purge the system and pull out the gases that are now in the soil around the landfill. How does the contractor/Army know that this is a sufficient time to accomplish this extraction?  The system should be measured on a greater frequency to determine with real data how the system is performing.

“This document has been funded partly or wholly through the use of U.S EPA Technical Assistance Grant Funds.  Its contents do not necessarily reflect the policies, actions or positions of the U.S. Environmental Protection Agency.  The Fort Ord Environmental Justice Network Inc. does not speak for nor represent the U.S. Environmental Protection Agency.”

Mention of  any trade name or commercial product or company does not constitute endorsement by any individual or party that prepared or sponsored this report.